## Sheet1
This list addresses and documents issues discovered in GIC sensors after filtering for known data issues, including: - delete repeated time points - delete station if all time points are empty - Find how many of the measurements differ from one time step to the next and delete station if on average measurements differ less than once in 5 minutes - remove repeat stations from files
Sensor | Event where noticed | Issue | Notes
10085 | 2015-09-19 | large variability but with bias to about 2 A
10198 | 2015-09-19 | negative offset from zero during the initial quiet phase of the storm before AE spikes; flips to positive GIC values during this quiet period, which exceeds 0.2 A and is called an event when it should not be; | other than issue of strange pre-event behavior, this station is fine
10377 | 2015-09-19 | strong bias to ~-3 A
10196 | 2015-09-19 | strong one day period swamps the GMD signal and creates problems for the event identification algorithm | candidate for systematic removal if this persists across events
10077 | 2015-09-19 | nonphysical nearly constant value for first 10 hours of the event until AE has a spike to ~1000 nT
10196 | 2015-03-17 | strong one day period swamps the GMD signal and creates problems for the event identification algorithm | candidate for systematic removal if this persists across events
10309 | 2015-03-17 | positive offset (does not contain any negative GICs ) | why would a sensor not have any negative GICs or have entirely one sign of GIC?
10075 | 2015-03-17 | large variability in measurements throughout
10198 | 2015-03-17 | large positive offset and one day period | candidate for systematic removal if this persists across events
10377 | 2015-03-17 | large variability in measurements throughout
10377 | 2015-12-20 | strong bias to ~-3 A
10198 | 2015-12-20 | shows long-period trend | candidate for systematic removal if this persists across events
10257 | 2015-12-20 | looks like small variance around ~-0.6 A
10063 | 2015-12-20 | digitized with small amplitude frequent jumping around ~-0.4 A
10326 | 2013-05-31 | shows long-period trend | this could be simply the natural variation in absence of strong perturbation at this sensor
10377 | 2013-05-31 | strong bias to ~-3 A | candidate for systematic removal because we observe this bias across all events and it is not caught by existing filtering techniques; NY coastal region
10257 | 2022-04-09 | strong bias to ~-3.2 A | candidate for systematic removal due to bias noticed across more than one event
10325 | 2022-04-09 | long data gap
10248 | 2022-04-09 | bias to ~1.5 A
10257 | 2018-08-25 | strong bias to ~-2 A | candidate for systematic removal due to bias noticed across more than one event
10423 | 2018-08-25 | strong bias to ~6 A
10398 | 2018-08-25 | bias with strange switching that moves to different bias throughout the event
10387 | 2018-08-25 | bias to ~-2.2 A
*Note that I only looked through the six events as representative sample